SAMSUNG

Project Report

Name : Mateusz Wielk

Telephone : +48 600 099 250

E-mail : m.wielk@partner.samsung.com

Address : Samsung Electronics Polska

UAM Fizyka

2020-10-20

1. Total Load Profile

1.1 UAM

| Dept | Fl | Room | Area |  | Load per unit area |  | Load |  |  | Sum of capacity |  |  | Model | Qty | Nominal Capacity |  |  | Outdoor | Model | Nominal Capacity |  | Combi. Ratio |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | CAD | SALES | Cooling | Heating | Cooling |  | Heating | Cooling |  | Heating |  |  | Cooling |  | Heating |  |  | Cooling | Heating | Cooling | Heating |
|  |  |  |  |  |  |  | TC | SHC | TC | TC | SHC | TC |  |  | TC | SHC | TC |  |  | TC | TC |  |  |
|  |  |  | m2 | m2 | kW/m2 | kW/m2 | kW | kW | kW | kW | kW | kW |  |  | kW | kW | kW | - | - | kW | kW | % | % |
| UAM | Piętro | Sala 1.19 | 205.689 | 205.69 | 0.25 | 0 | 50.40 | 0.00 | 0.00 | 50.4 | 37.8 | 56.7 | AM056HNMPKH/EU | 9 | 5.60 | 4.20 | 6.30 | System VRF 1.19 | AM180JXVHGH/ET | 50.40 | 56.70 | 100 | 100 |
|  |  | Sala 1.20 | 205.325 | 205.32 | 0.25 | 0 | 50.40 | 0.00 | 0.00 | 50.4 | 37.8 | 56.7 | AM056HNMPKH/EU | 9 | 5.60 | 4.20 | 6.30 | System VRF 1.20 | AM180JXVHGH/ET | 50.40 | 56.70 | 100 | 100 |

2. Piping & Wiring

2.1 System VRF 1.19

2.1.1 Detail Load Profile

1) Design condition: Poland, POZNAN, Cooling 30, Heating -18

2) Load profile

| Building |  |  | Unit |  | Liquid Pipe | Gas Pipe | H.P.Gas Pipe | Airflow |  | Design condition : Indoor |  | Max. Capacity @design condition |  |  | Simultaneous Operation Capacity |  |  | Combination Ratio |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Dept | Fl | Room | Name | Model name |  |  |  |  |  | Cooling WB.Temp | Heating DB.Temp | Cooling |  | Heating | Cooling |  | Heating | Cooling | Heating |
|  |  |  |  |  |  |  |  |  |  |  |  | TC | SHC | TC | TC | SHC | TC |  |  |
| - | - | - | - | - | Ø, mm | Ø, mm | Ø, mm | Mode | CMM | °C | °C | kW | kW | kW | kW | kW | kW | % | % |
| UAM | Dach |  | System VRF 1.19 | AM180JXVHGH/ET | 15.88 | 28.58 |  |  | 290.00 |  |  | 49.21 |  | 44.65 | 49.21 |  | 44.65 | 100 | 100 |
|  | Piętro | Sala 1.19 | Sala 1.19_1 | AM056HNMPKH/EU | 6.35 | 12.70 |  | H | 16.00 | 19 | 20 | 5.60 | 4.20 | 6.30 | 5.47 | 4.10 | 4.96 |  |  |
|  |  | Sala 1.19 | Sala 1.19_2 | AM056HNMPKH/EU | 6.35 | 12.70 |  | H | 16.00 | 19 | 20 | 5.60 | 4.20 | 6.30 | 5.47 | 4.10 | 4.96 |  |  |
|  |  | Sala 1.19 | Sala 1.19_3 | AM056HNMPKH/EU | 6.35 | 12.70 |  | H | 16.00 | 19 | 20 | 5.60 | 4.20 | 6.30 | 5.47 | 4.10 | 4.96 |  |  |
|  |  | Sala 1.19 | Sala 1.19_4 | AM056HNMPKH/EU | 6.35 | 12.70 |  | H | 16.00 | 19 | 20 | 5.60 | 4.20 | 6.30 | 5.47 | 4.10 | 4.96 |  |  |
|  |  | Sala 1.19 | Sala 1.19_5 | AM056HNMPKH/EU | 6.35 | 12.70 |  | H | 16.00 | 19 | 20 | 5.60 | 4.20 | 6.30 | 5.47 | 4.10 | 4.96 |  |  |
|  |  | Sala 1.19 | Sala 1.19_6 | AM056HNMPKH/EU | 6.35 | 12.70 |  | H | 16.00 | 19 | 20 | 5.60 | 4.20 | 6.30 | 5.47 | 4.10 | 4.96 |  |  |
|  |  | Sala 1.19 | Sala 1.19_7 | AM056HNMPKH/EU | 6.35 | 12.70 |  | H | 16.00 | 19 | 20 | 5.60 | 4.20 | 6.30 | 5.47 | 4.10 | 4.96 |  |  |
|  |  | Sala 1.19 | Sala 1.19_8 | AM056HNMPKH/EU | 6.35 | 12.70 |  | H | 16.00 | 19 | 20 | 5.60 | 4.20 | 6.30 | 5.47 | 4.10 | 4.96 |  |  |
|  |  | Sala 1.19 | Sala 1.19_9 | AM056HNMPKH/EU | 6.35 | 12.70 |  | H | 16.00 | 19 | 20 | 5.60 | 4.20 | 6.30 | 5.47 | 4.10 | 4.96 |  |  |

2.1.2 Control

1) This data is for reference only. Verify local, state, and national electric codes. Samsung does not guarantee this data.

2) Configuration

| Building |  |  | Unit |  | Communication wires | Power wires | Breaker Fuse | Main Address |  | RMC Address |  | Accessories |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Dept | Fl | Room | Name | Model name |  |  |  |  |  |  |  | Optional accessories | Basic accessories |
| - | - | - | - | - | mm2 | mm2 | A |  |  |  |  |  |  |
| UAM | Dach |  | System VRF 1.19 | AM180JXVHGH/ET | 0.75~ | ~ | 50 |  |  |  |  |  |  |
|  | Piętro | Sala 1.19 | Sala 1.19_1 | AM056HNMPKH/EU | 0.75~1.5 | 1.5~2.5 |  | 0 | 2 | 0 | 0 | MCM-A300N | MCM-A300N |
|  |  | Sala 1.19 | Sala 1.19_2 | AM056HNMPKH/EU | 0.75~1.5 | 1.5~2.5 |  | 0 | 1 | 0 | 0 |  |  |
|  |  | Sala 1.19 | Sala 1.19_3 | AM056HNMPKH/EU | 0.75~1.5 | 1.5~2.5 |  | 0 | 0 | 0 | 0 |  |  |
|  |  | Sala 1.19 | Sala 1.19_4 | AM056HNMPKH/EU | 0.75~1.5 | 1.5~2.5 |  | 0 | 5 | 0 | 0 |  |  |
|  |  | Sala 1.19 | Sala 1.19_5 | AM056HNMPKH/EU | 0.75~1.5 | 1.5~2.5 |  | 0 | 4 | 0 | 0 |  |  |
|  |  | Sala 1.19 | Sala 1.19_6 | AM056HNMPKH/EU | 0.75~1.5 | 1.5~2.5 |  | 0 | 3 | 0 | 0 |  |  |
|  |  | Sala 1.19 | Sala 1.19_7 | AM056HNMPKH/EU | 0.75~1.5 | 1.5~2.5 |  | 0 | 8 | 0 | 0 |  |  |
|  |  | Sala 1.19 | Sala 1.19_8 | AM056HNMPKH/EU | 0.75~1.5 | 1.5~2.5 |  | 0 | 7 | 0 | 0 |  |  |
|  |  | Sala 1.19 | Sala 1.19_9 | AM056HNMPKH/EU | 0.75~1.5 | 1.5~2.5 |  | 0 | 6 | 0 | 0 |  |  |

2.1.3 Equipment list

1) Equipment list

| Categories | Model name |  | Qty | Categories | Model name |  | Qty |
| --- | --- | --- | --- | --- | --- | --- | --- |
| DVM S(NEW) |  | AM180JXVHGH/ET | 1 | Y-Joint |  | MXJ-YA2512M | 4 |
| DUCT S |  | AM056HNMPKH/EU | 9 | Y-Joint |  | MXJ-YA1509M | 3 |
| Y-Joint |  | MXJ-YA2815M | 1 |  |  |  |  |

2) Piping length

| Length as pipe diameter |  | 6.35 | 9.52 | 12.70 | 15.88 | 19.05 | 22.22 |  | 25.40 | 28.58 | 31.75 | 34.92 | 38.10 |  | 41.28 | 44.45 | 47.63 | 50.80 | 53.98 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1. Liquid piping | m | 15.39 | 16.39 | 5.52 | 3.72 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2. Gas piping | m |  |  | 15.39 | 8.97 | 7.42 |  |  |  | 9.25 |  |  |  |  |  |  |  |  |  |
| 3. High pressure gas piping | m |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Restriction of pipe length |  | Restriction (Based on installation manual) |  |  |  |  |  | Actual piping length |  |  |  |  |  | Equivalent piping length |  |  |  |  |  |
| 1. Total piping length | m | 1000.00 |  |  |  |  |  | 43.43 |  |  |  |  |  |  |  |  |  |  |  |
| 2. Maximum piping length | m | 200.00 |  |  |  |  |  | 23.60 |  |  |  |  |  | 26.05 |  |  |  |  |  |
| 3. Main pipe length | m |  |  |  |  |  |  | 3.72 |  |  |  |  |  |  |  |  |  |  |  |
| 4. Piping length between the first branch and the farthest indoor unit | m | 45.00/90.00 |  |  |  |  |  | 19.88 |  |  |  |  |  |  |  |  |  |  |  |
| 5. Level difference between outdoor and indoor unit(Max) (OD above ID unit / OD below ID unit) | m | 40.00/110.00 |  |  |  |  |  | 2.00 |  |  |  |  |  |  |  |  |  |  |  |
| 6. Level difference between indoor units | m | 50.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

3) Basic and additional charging ref. amount

Basic (Factory) charge ref. amount : 8.400 kg

Additional Field charging ref. amount : 4.830 kg

Total number of bendings : 17

2.1.4 Piping

- The system configuration may be different from the actual installation conditions, refer to the installation manual.

2.2 System VRF 1.20

2.2.1 Detail Load Profile

1) Design condition: Poland, POZNAN, Cooling 30, Heating -18

2) Load profile

| Building |  |  | Unit |  | Liquid Pipe | Gas Pipe | H.P.Gas Pipe | Airflow |  | Design condition : Indoor |  | Max. Capacity @design condition |  |  | Simultaneous Operation Capacity |  |  | Combination Ratio |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Dept | Fl | Room | Name | Model name |  |  |  |  |  | Cooling WB.Temp | Heating DB.Temp | Cooling |  | Heating | Cooling |  | Heating | Cooling | Heating |
|  |  |  |  |  |  |  |  |  |  |  |  | TC | SHC | TC | TC | SHC | TC |  |  |
| - | - | - | - | - | Ø, mm | Ø, mm | Ø, mm | Mode | CMM | °C | °C | kW | kW | kW | kW | kW | kW | % | % |
| UAM | Dach |  | System VRF 1.20 | AM180JXVHGH/ET | 15.88 | 28.58 |  |  | 290.00 |  |  | 49.35 |  | 44.65 | 49.35 |  | 44.65 | 100 | 100 |
|  | Piętro | Sala 1.20 | Sala 1.20_1 | AM056HNMPKH/EU | 6.35 | 12.70 |  | H | 16.00 | 19 | 20 | 5.60 | 4.20 | 6.30 | 5.48 | 4.11 | 4.96 |  |  |
|  |  | Sala 1.20 | Sala 1.20_2 | AM056HNMPKH/EU | 6.35 | 12.70 |  | H | 16.00 | 19 | 20 | 5.60 | 4.20 | 6.30 | 5.48 | 4.11 | 4.96 |  |  |
|  |  | Sala 1.20 | Sala 1.20_3 | AM056HNMPKH/EU | 6.35 | 12.70 |  | H | 16.00 | 19 | 20 | 5.60 | 4.20 | 6.30 | 5.48 | 4.11 | 4.96 |  |  |
|  |  | Sala 1.20 | Sala 1.20_4 | AM056HNMPKH/EU | 6.35 | 12.70 |  | H | 16.00 | 19 | 20 | 5.60 | 4.20 | 6.30 | 5.48 | 4.11 | 4.96 |  |  |
|  |  | Sala 1.20 | Sala 1.20_5 | AM056HNMPKH/EU | 6.35 | 12.70 |  | H | 16.00 | 19 | 20 | 5.60 | 4.20 | 6.30 | 5.48 | 4.11 | 4.96 |  |  |
|  |  | Sala 1.20 | Sala 1.20_6 | AM056HNMPKH/EU | 6.35 | 12.70 |  | H | 16.00 | 19 | 20 | 5.60 | 4.20 | 6.30 | 5.48 | 4.11 | 4.96 |  |  |
|  |  | Sala 1.20 | Sala 1.20_7 | AM056HNMPKH/EU | 6.35 | 12.70 |  | H | 16.00 | 19 | 20 | 5.60 | 4.20 | 6.30 | 5.48 | 4.11 | 4.96 |  |  |
|  |  | Sala 1.20 | Sala 1.20_8 | AM056HNMPKH/EU | 6.35 | 12.70 |  | H | 16.00 | 19 | 20 | 5.60 | 4.20 | 6.30 | 5.48 | 4.11 | 4.96 |  |  |
|  |  | Sala 1.20 | Sala 1.20_9 | AM056HNMPKH/EU | 6.35 | 12.70 |  | H | 16.00 | 19 | 20 | 5.60 | 4.20 | 6.30 | 5.48 | 4.11 | 4.96 |  |  |

2.2.2 Control

1) This data is for reference only. Verify local, state, and national electric codes. Samsung does not guarantee this data.

2) Configuration

| Building |  |  | Unit |  | Communication wires | Power wires | Breaker Fuse | Main Address |  | RMC Address |  | Accessories |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Dept | Fl | Room | Name | Model name |  |  |  |  |  |  |  | Optional accessories | Basic accessories |
| - | - | - | - | - | mm2 | mm2 | A |  |  |  |  |  |  |
| UAM | Dach |  | System VRF 1.20 | AM180JXVHGH/ET | 0.75~ | ~ | 50 |  |  |  |  |  |  |
|  | Piętro | Sala 1.20 | Sala 1.20_1 | AM056HNMPKH/EU | 0.75~1.5 | 1.5~2.5 |  | 0 | 8 | 0 | 0 | MCM-A300N | MCM-A300N |
|  |  | Sala 1.20 | Sala 1.20_2 | AM056HNMPKH/EU | 0.75~1.5 | 1.5~2.5 |  | 0 | 7 | 0 | 0 |  |  |
|  |  | Sala 1.20 | Sala 1.20_3 | AM056HNMPKH/EU | 0.75~1.5 | 1.5~2.5 |  | 0 | 6 | 0 | 0 |  |  |
|  |  | Sala 1.20 | Sala 1.20_4 | AM056HNMPKH/EU | 0.75~1.5 | 1.5~2.5 |  | 0 | 5 | 0 | 0 |  |  |
|  |  | Sala 1.20 | Sala 1.20_5 | AM056HNMPKH/EU | 0.75~1.5 | 1.5~2.5 |  | 0 | 4 | 0 | 0 |  |  |
|  |  | Sala 1.20 | Sala 1.20_6 | AM056HNMPKH/EU | 0.75~1.5 | 1.5~2.5 |  | 0 | 3 | 0 | 0 |  |  |
|  |  | Sala 1.20 | Sala 1.20_7 | AM056HNMPKH/EU | 0.75~1.5 | 1.5~2.5 |  | 0 | 2 | 0 | 0 |  |  |
|  |  | Sala 1.20 | Sala 1.20_8 | AM056HNMPKH/EU | 0.75~1.5 | 1.5~2.5 |  | 0 | 1 | 0 | 0 |  |  |
|  |  | Sala 1.20 | Sala 1.20_9 | AM056HNMPKH/EU | 0.75~1.5 | 1.5~2.5 |  | 0 | 0 | 0 | 0 |  |  |

2.2.3 Equipment list

1) Equipment list

| Categories | Model name |  | Qty | Categories | Model name |  | Qty |
| --- | --- | --- | --- | --- | --- | --- | --- |
| DVM S(NEW) |  | AM180JXVHGH/ET | 1 | Y-Joint |  | MXJ-YA2512M | 4 |
| DUCT S |  | AM056HNMPKH/EU | 9 | Y-Joint |  | MXJ-YA1509M | 3 |
| Y-Joint |  | MXJ-YA2815M | 1 |  |  |  |  |

2) Piping length

| Length as pipe diameter |  | 6.35 | 9.52 | 12.70 | 15.88 | 19.05 | 22.22 |  | 25.40 | 28.58 | 31.75 | 34.92 | 38.10 |  | 41.28 | 44.45 | 47.63 | 50.80 | 53.98 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1. Liquid piping | m | 14.83 | 18.60 | 4.13 | 2.36 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2. Gas piping | m |  |  | 14.83 | 10.30 | 8.30 |  |  |  | 6.49 |  |  |  |  |  |  |  |  |  |
| 3. High pressure gas piping | m |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Restriction of pipe length |  | Restriction (Based on installation manual) |  |  |  |  |  | Actual piping length |  |  |  |  |  | Equivalent piping length |  |  |  |  |  |
| 1. Total piping length | m | 1000.00 |  |  |  |  |  | 42.32 |  |  |  |  |  |  |  |  |  |  |  |
| 2. Maximum piping length | m | 200.00 |  |  |  |  |  | 20.80 |  |  |  |  |  | 22.65 |  |  |  |  |  |
| 3. Main pipe length | m |  |  |  |  |  |  | 2.36 |  |  |  |  |  |  |  |  |  |  |  |
| 4. Piping length between the first branch and the farthest indoor unit | m | 45.00/90.00 |  |  |  |  |  | 18.44 |  |  |  |  |  |  |  |  |  |  |  |
| 5. Level difference between outdoor and indoor unit(Max) (OD above ID unit / OD below ID unit) | m | 40.00/110.00 |  |  |  |  |  | 2.00 |  |  |  |  |  |  |  |  |  |  |  |
| 6. Level difference between indoor units | m | 50.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

3) Basic and additional charging ref. amount

Basic (Factory) charge ref. amount : 8.400 kg

Additional Field charging ref. amount : 4.530 kg

Total number of bendings : 18

2.2.4 Piping

- The system configuration may be different from the actual installation conditions, refer to the installation manual.

3. Specification

3.1 DVM

3.1.1 Outdoor units

| Model name |  |  |  | AM180JXVHGH/ET |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Power supply |  |  | Ø, #, V, Hz | 3,4,380-415,50Hz |  |  |
| Mode |  |  | - | HEAT PUMP |  |  |
| Performance | HP/TON |  | HP/TON | 18/14.33 |  |  |
|  | Capacity(Nominal) | Cooling | kW | 50.4 |  |  |
|  |  |  | Kcal/h | 43340 |  |  |
|  |  | Cooling 46°C | kW | - |  |  |
|  |  |  | Kcal/h | N/A |  |  |
|  |  | Heating | kW | 56.7 |  |  |
|  |  |  | Kcal/h | 48760 |  |  |
|  | -20 °C | Heating(Low ambient temp.) | kW | - |  |  |
|  |  |  | Kcal/h | N/A |  |  |
| Power | Power Input(Nominal) | Cooling | kW | 12.32 |  |  |
|  |  | Heating | kW | 12.01 |  |  |
|  | Power Input (at specific) |  | kW | N/A |  |  |
|  | Current Input(Nominal) | Cooling | A | 19.8 |  |  |
|  |  | Heating | A | 19.3 |  |  |
|  | Max. Current Input |  | A | 39.2 |  |  |
|  | Circuit Breaker |  | A | 50 |  |  |
| COP | Cooling |  | - | 4.09 |  |  |
|  | Heating |  | W/W | 4.72 |  |  |
| Compressor | Type |  | - | SSC Scrollx2 |  |  |
|  | Output |  | kW × n | 6.39x2 |  |  |
| Fan | Type |  | - | Propeller |  |  |
|  | Output |  | W | 620x2 |  |  |
|  | Number of Units |  | EA | 2 |  |  |
|  | Air Flow Rate |  | CMM | 290.00 |  |  |
|  | External Static Pressure | Max. | mmAq | 8 |  |  |
| Piping Connections | Liquid Pipe |  | Ø,mm(in) | 15.88(5/8") |  |  |
|  | Gas Pipe |  | Ø,mm(in) | 28.58(1 1/8") |  |  |
|  | Discharge Gas Pipe |  | Ø,mm(in) | -(-) |  |  |
|  | Oil Equalizing Pipe |  | Ø,mm(in) | N/A(N/A) |  |  |
| Field Wiring | Power Source Wire |  | mm2 | - |  |  |
|  | Transmission Cable |  | mm2 | 0.75/ |  |  |
| Refrigerant | Type |  | - | R410A |  |  |
|  | Factory Charging |  | kg | 8.400 |  |  |
| Sound | Sound pressure |  | dB(A) | 63 |  |  |
| External Dimension | Net Weight |  | kg | 293.000 |  |  |
|  | Shipping Weight |  | kg | 312.000 |  |  |
|  | Net Dimensions (WxHxD) |  | mm | 1295.00x1695.00x765.00 |  |  |
|  | Shipping Dimensions (WxHxD) |  | mm | 1363.00x1887.00x832.00 |  |  |
| Operating Temp. Range | Cooling |  | °C | -5.00~48.00 |  |  |
|  | Heating |  | °C | -25.00~24.00 |  |  |

3.1.2 Indoor units

| Model |  |  |  | AM056HNMPKH/EU |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Power supply |  |  | Ø, #, V, Hz | 1,2,220-240,50Hz |  |  |  |  |
| Performance | Capacity(Nominal) | Cooling | kW | 5.6 |  |  |  |  |
|  |  |  | Kcal/h | 4820 |  |  |  |  |
|  |  | Cooling (SHC) | kW | 4.2 |  |  |  |  |
|  |  |  | Kcal/h | 3610 |  |  |  |  |
|  |  | Heating | kW | 6.3 |  |  |  |  |
|  |  |  | Kcal/h | 5420 |  |  |  |  |
| Power | Power Input(Nominal) | Cooling | W | 70 |  |  |  |  |
|  |  | Heating |  | 70 |  |  |  |  |
|  | Current Input | Cooling | A | 0.7 |  |  |  |  |
|  |  | Heating |  | 0.7 |  |  |  |  |
| Fan | Motor | Type | - | Sirocco Fan |  |  |  |  |
|  |  | Output | W | 153 |  |  |  |  |
|  |  | Number of unit | EA | 1 |  |  |  |  |
|  | Air Flow Rate | H/M/L (UL) | CMM | 16.00/13.50/11.00 |  |  |  |  |
|  | External Pressure | Min / Std / Max | mmAq | 0.00 / 3.00 / 15.00 |  |  |  |  |
| Piping Connections | Liquid Pipe |  | Ø,mm(in) | 6.35(1/4") |  |  |  |  |
|  | Gas Pipe |  | Ø,mm(in) | 12.7(1/2") |  |  |  |  |
|  | Drain Pipe |  | Ø,mm | VP25 (OD 32,ID 25) |  |  |  |  |
| Field Wiring | Power Source Wire |  | mm2 | 1.5~2.5 |  |  |  |  |
|  | Transmission Cable |  | mm2 | 0.75/1.5 |  |  |  |  |
| Refrigerant | Type |  | - | R410A |  |  |  |  |
|  | Control Method |  | - | EEV INCLUDED |  |  |  |  |
| Sound | Sound pressure | High / Low | dBA | 33/27 |  |  |  |  |
| Dimensions | Net Weight |  | kg | 25.500 |  |  |  |  |
|  | Shipping Weight |  | kg | 30.000 |  |  |  |  |
|  | Net Dimensions (WxHxD) |  | mm | 850.00x250.00x700.00 |  |  |  |  |
|  | Shipping Dimensions (WxHxD) |  | mm | 1064.00x320.00x784.00 |  |  |  |  |
| Panel Size | Panel model |  | - |  |  |  |  |  |
|  | Panel Net Weight |  | kg |  |  |  |  |  |
|  | Shipping Weight |  | kg |  |  |  |  |  |
|  | Net Dimensions (WxHxD) |  | mm |  |  |  |  |  |
|  | Shipping Dimensions (WxHxD) |  | mm |  |  |  |  |  |

4. Total Equipment List

| Index | Model | Qty | Remark(Categories) | Unit Price | Amount |
| --- | --- | --- | --- | --- | --- |
| Outdoor unit | AM180JXVHGH/ET | 2 | DVM S(NEW) | 0 | 0 |
| Indoor unit | AM056HNMPKH/EU | 18 | DUCT S | 0 | 0 |
| Piping | MXJ-YA2815M | 2 | Y-Joint | 0 | 0 |
|  | MXJ-YA2512M | 8 | Y-Joint | 0 | 0 |
|  | MXJ-YA1509M | 6 | Y-Joint | 0 | 0 |
| Optional accessories | MCM-A300N | 2 | CONTROLLER | 0 | 0 |
| Ref. Pipe | 6.35(1/4") | 30.22 | m | 0 | 0 |
|  | 9.52(3/8") | 34.99 | m | 0 | 0 |
|  | 12.70(1/2") | 39.87 | m | 0 | 0 |
|  | 15.88(5/8") | 25.35 | m | 0 | 0 |
|  | 19.05(3/4") | 15.72 | m | 0 | 0 |
|  | 28.58(1 1/8") | 15.74 | m | 0 | 0 |
| Additional Ref. Amount | R410A | 9.36 | kg | 0 | 0 |
| Total |  |  |  |  | 0 |